## Slave registers
Modbus slave address 10			Holding	Input	Description
implemented registers			1-125	1-125
register area			1-25	1-25	Inductive Power registers
register area			26-50	26-50	RF 1 device info (for example 16 channel thermocouple) : modbus register 26 => register 1 of the device implementation
register area			51-75	51-75	RF 2 device info (for example 16 channel thermocouple) : modbus register 51 => register 1 of the device implementation
register area			76-100	76-100	RF 3 device info (for example 16 channel thermocouple) : modbus register 76 => register 1 of the device implementation
register area			101-125	101-125	RF 4 device info (for example 16 channel thermocouple) : modbus register 101 => register 1 of the device implementation

Modbus slave address 11			Holding	Input	Description
implemented registers			1-25	1-25
register area			1-25	1-25	RF 1 device info (for example 16 channel thermocouple)

Modbus slave address 12			Holding	Input	Description
implemented registers			1-25	1-25
register area			1-25	1-25	RF 2 device info (for example 16 channel thermocouple)

Modbus slave address 13			Holding	Input	Description
implemented registers			1-25	1-25
register area			1-25	1-25	RF 3 device info (for example 16 channel thermocouple)

Modbus slave address 14			Holding	Input	Description
implemented registers			1-25	1-25
register area			1-25	1-25	RF 4 device info (for example 16 channel thermocouple)

## Device register implementations
Wireless Inductive Power Supply registers
Register	Value	Description
1	Uin	Inductive power input voltage [0,01V]
2	1 ch Uout	channel 1 output voltage [0,01V]
3	1 ch Iout	channel 1 output current [0,01A]
4	1 ch Iout filtered	channel 1 output current, filtered cut off frequency 6,5 Hz [0,01A]
5	2 ch Uout	channel 2 output voltage [0,01V]
6	2 ch Iout	channel 2 output current [0,01A]
7	2 ch Iout filtered	channel 2 output current, filtered cut off frequency 6,5 Hz [0,01A]
8	3 ch Uout	channel 3 output voltage [0,01V]
9	3 ch Iout	channel 3 output current [0,01A]
10	3 ch Iout filtered	channel 3 output current, filtered cut off frequency 6,5 Hz [0,01A]
11	4 ch Uout	channel 4 output voltage [0,01V]
12	4 ch Iout	channel 4 output current [0,01A]
13	4 ch Iout filtered	channel 4 output current, filtered cut off frequency 6,5 Hz [0,01A]
14	Reserved
15	Reserved
16	Reserved
17	Reserved
18	Reserved
19	Reserved
20	Reserved
21	Reserved
22	Reserved
23	Reserved
24	Reserved
25	Reserved

16 Channe Thermocouple registers
Register	Value	Description
1	1 ch Temperature	Temperature [1/16 °C]
2	2 ch Temperature	Temperature [1/16 °C]
3	3 ch Temperature	Temperature [1/16 °C]
4	4 ch Temperature	Temperature [1/16 °C]
5	5 ch Temperature	Temperature [1/16 °C]
6	6 ch Temperature	Temperature [1/16 °C]
7	7 ch Temperature	Temperature [1/16 °C]
8	8 ch Temperature	Temperature [1/16 °C]
9	9 ch Temperature	Temperature [1/16 °C]
10	10 ch Temperature	Temperature [1/16 °C]
11	11 ch Temperature	Temperature [1/16 °C]
12	12 ch Temperature	Temperature [1/16 °C]
13	13 ch Temperature	Temperature [1/16 °C]
14	14 ch Temperature	Temperature [1/16 °C]
15	15 ch Temperature	Temperature [1/16 °C]
16	16 ch Temperature	Temperature [1/16 °C]
17	Reserved
18	Reserved
19	Reserved
20	Reserved
21	Rx packet index	Running index of received packet
22	Rx status	current status of the receivers: 0 if no packet received, 1 if RF 1 received, 2 if RF 2 received, 3 if both received
23	Rx success ratio	indicates ratio of successfully received packets per second: 100 if all packet received, 0 if no packet received
24	Reserved
25	Reserved