## Slave registers
Modbus slave address 10 | Holding | Input | Description
implemented registers | 1-125 | 1-125
register area | 1-25 | 1-25 | Inductive Power registers
register area | 26-50 | 26-50 | RF 1 device info (for example 16 channel thermocouple) : modbus register 26 => register 1 of the device implementation
register area | 51-75 | 51-75 | RF 2 device info (for example 16 channel thermocouple) : modbus register 51 => register 1 of the device implementation
register area | 76-100 | 76-100 | RF 3 device info (for example 16 channel thermocouple) : modbus register 76 => register 1 of the device implementation
register area | 101-125 | 101-125 | RF 4 device info (for example 16 channel thermocouple) : modbus register 101 => register 1 of the device implementation
register area | 126-150 | 126-150 | RF 5 device info (for example 16 channel thermocouple) : modbus register 101 => register 1 of the device implementation
register area | 151-175 | 151-175 | RF 6 device info (for example 16 channel thermocouple) : modbus register 101 => register 1 of the device implementation
Modbus slave address 11 | Holding | Input | Description
implemented registers | 1-25 | 1-25
register area | 1-25 | 1-25 | RF 1 device info (for example 16 channel thermocouple)
Modbus slave address 12 | Holding | Input | Description
implemented registers | 1-25 | 1-25
register area | 1-25 | 1-25 | RF 2 device info (for example 16 channel thermocouple)
Modbus slave address 13 | Holding | Input | Description
implemented registers | 1-25 | 1-25
register area | 1-25 | 1-25 | RF 3 device info (for example 16 channel thermocouple)
Modbus slave address 14 | Holding | Input | Description
implemented registers | 1-25 | 1-25
register area | 1-25 | 1-25 | RF 4 device info (for example 16 channel thermocouple)
Modbus slave address 15 | Holding | Input | Description
implemented registers | 1-25 | 1-25
register area | 1-25 | 1-25 | RF 5 device info (for example 16 channel thermocouple)
Modbus slave address 16 | Holding | Input | Description
implemented registers | 1-25 | 1-25
register area | 1-25 | 1-25 | RF 6 device info (for example 16 channel thermocouple)

## Device register implementations
Wireless Inductive Power Supply registers
Register | Value | Description
1 | Uin | Inductive power input voltage [0,01V]
2 | 1 ch Uout | channel 1 output voltage [0,01V]
3 | 1 ch Iout | channel 1 output current [0,01A]
4 | 1 ch Iout filtered | channel 1 output current, filtered cut off frequency 6,5 Hz [0,01A]
5 | 2 ch Uout | channel 2 output voltage [0,01V]
6 | 2 ch Iout | channel 2 output current [0,01A]
7 | 2 ch Iout filtered | channel 2 output current, filtered cut off frequency 6,5 Hz [0,01A]
8 | 3 ch Uout | channel 3 output voltage [0,01V]
9 | 3 ch Iout | channel 3 output current [0,01A]
10 | 3 ch Iout filtered | channel 3 output current, filtered cut off frequency 6,5 Hz [0,01A]
11 | 4 ch Uout | channel 4 output voltage [0,01V]
12 | 4 ch Iout | channel 4 output current [0,01A]
13 | 4 ch Iout filtered | channel 4 output current, filtered cut off frequency 6,5 Hz [0,01A]
14 | Reserved
15 | Reserved
16 | Reserved
17 | Reserved
18 | Reserved
19 | Reserved
20 | Reserved
21 | Reserved
22 | Reserved
23 | Reserved
24 | Reserved
25 | Reserved
16 Channe Thermocouple registers
Register | Value | Description
1 | 1 ch Temperature | Temperature [1/16 °C]
2 | 2 ch Temperature | Temperature [1/16 °C]
3 | 3 ch Temperature | Temperature [1/16 °C]
4 | 4 ch Temperature | Temperature [1/16 °C]
5 | 5 ch Temperature | Temperature [1/16 °C]
6 | 6 ch Temperature | Temperature [1/16 °C]
7 | 7 ch Temperature | Temperature [1/16 °C]
8 | 8 ch Temperature | Temperature [1/16 °C]
9 | 9 ch Temperature | Temperature [1/16 °C]
10 | 10 ch Temperature | Temperature [1/16 °C]
11 | 11 ch Temperature | Temperature [1/16 °C]
12 | 12 ch Temperature | Temperature [1/16 °C]
13 | 13 ch Temperature | Temperature [1/16 °C]
14 | 14 ch Temperature | Temperature [1/16 °C]
15 | 15 ch Temperature | Temperature [1/16 °C]
16 | 16 ch Temperature | Temperature [1/16 °C]
17 | Reserved
18 | Reserved
19 | Reserved
20 | Reserved
21 | Rx packet index | Running index of received packet
22 | Rx status | current status of the receivers: 0 if no packet received, 1 if RF 1 received, 2 if RF 2 received, 3 if both received
23 | Rx success ratio | indicates ratio of successfully received packets per second: 100 if all packet received, 0 if no packet received
24 | Reserved
25 | Reserved